## Input
AREA | Recommended_Variable | Current_IO | DataType | Signal_Class | Direction | Description_EN
M1-M2 | xPhaseProtectionRelaySig | X0.0 | BOOL | DI | Input | Machine 1-2 protection relay signal
M1-M2 | xSafetySignal | X0.1 | BOOL | DI | Input | PILZ safety input
M1-M2 | xEmgStop1 | X0.2 | BOOL | DI | Input | Emergency -P -S6 signal
M1-M2 | xEmgStop2 | X0.3 | BOOL | DI | Input | Emergency M1A M1B -S6 -S7 signal
M1-M2 | xEmgStop3 | X0.4 | BOOL | DI | Input | Emergency M2A M2B -S6 -S7 signal
M1 | xM1EvapMotRun | X0.5 | BOOL | DI | Input | Machine 1 evaporator water pump running feedback
M1 | xM1CondenserMotRun | X0.6 | BOOL | DI | Input | Machine 1 condenser water pump running feedback
M1 | xM1ExhaustFanRun | X0.7 | BOOL | DI | Input | Machine 1 exhaust fun running feedback
M1 | xM1CompDriveRun | X0.8 | BOOL | DI | Input | Machine 1 compressor inverter run feedback
M1 | xM1CompDriveFault | X0.9 | BOOL | DI | Input | Machine 1 compressor inverter fault feedback
M1 | xM1LiquidLowLevelSw | X0.10 | BOOL | DI | Input | Machine 1 liquid low level switch
M1 | xM1LiquidHighLevelSw | X0.11 | BOOL | DI | Input | Machine 1 liquid high level switch
M2 | xM2EvapMotRun | X0.12 | BOOL | DI | Input | Machine 2 evaporator water pump running feedback
M2 | xM2CondenserMotRun | X0.13 | BOOL | DI | Input | Machine 2 condenser water pump running feedback
M2 | xM2ExhaustFanRun | X0.14 | BOOL | DI | Input | Machine 2 exhaust fun running feedback
M2 | xM2CompDriveRun | X0.15 | BOOL | DI | Input | Machine 2 compressor inverter run feedback
M2 | xM2CompDriveFault | X0.16 | BOOL | DI | Input | Machine 2 compressor inverter fault feedback
M2 | xM2LiquidLowLevelSw | X0.17 | BOOL | DI | Input | Machine 2 liquid low level switch
M2 | xM2LiquidHighLevelSw | X0.18 | BOOL | DI | Input | Machine 2 liquid high level switch
M1 | xM1OilFlowSw | X0.19 | BOOL | DI | Input | Machine 1 oil flow switch
M1 | xM1HighPressureSw | X0.20 | BOOL | DI | Input | Machine 1 high pressure switch
M1 | xM1LowPressureSw | X0.21 | BOOL | DI | Input | Machine 1 low pressure switch
M1 | xM1OilTankLowLevelSw | X0.22 | BOOL | DI | Input | Machine 1 oil tank low level switch
M2 | xM2OilFlowSw | X0.23 | BOOL | DI | Input | Machine 2 oil flow switch
M2 | xM2HighPressureSw | X0.24 | BOOL | DI | Input | Machine 2 high pressure switch
M2 | xM2LowPressureSw | X0.25 | BOOL | DI | Input | Machine 2 low pressure switch
M2 | xM2OilTankLowLevelSw | X0.26 | BOOL | DI | Input | Machine 2 oil tank low level switch
M1 | xM1BmsStartCoolEnableIn | X0.27 | BOOL | DI | Input | Machine 1 external BMS cool start enable input
M1 | xM1BmsStartHeatEnableIn | X0.28 | BOOL | DI | Input | Machine 1 external BMS heat start enable input
M2 | xM2BmsStartCoolEnableIn | X0.29 | BOOL | DI | Input | Machine 2 external BMS cool start enable input
M2 | xM2BmsStartHeatEnableIn | X0.30 | BOOL | DI | Input | Machine 2 external BMS heat start enable input
M1 | xM1EvapFlowSw | X0.31 | BOOL | DI | Input | Machine 1 evaporator flow switch feedback
M2 | xM2EvapFlowSw | X0.32 | BOOL | DI | Input | Machine 2 evaporator flow switch feedback
M1 | xM1GasFault | X0.33 | BOOL | DI | Input | Machine 1 gas alarm signal | Bu iki sinyal müşteri tarafında çektirilecek. Ondan rölenin A1-A2 uçları direkt aşağı inilecek. Kontak tarafı plc'ye girilecektir.
M2 | xM2GasFault | X0.34 | BOOL | DI | Ipnut | Machine 2 gas alarm signal

## Output
AREA | Recommended_Variable | Current_IO | DataType | Signal_Class | Direction | Description_EN
M1 | xM1EvapPumpCmd | Y0.0 | BOOL | DO | Output | Machine 1 evaporator pump command
M1 | xM1CondPumpCmd | Y0.1 | BOOL | DO | Output | Machine 1 condenser pump command
M1 | xM1ExhaustFanCmd | Y0.2 | BOOL | DO | Output | Machine 1 machine room exhaust fan command
M1 | xM1CompRunCmd | Y0.3 | BOOL | DO | Output | Machine 1 compressor run output signal
M1 | xM1TwoWayValveCmd | Y0.3 | BOOL | DO | Output | Machine 1 two-way valve command
M1 | xM1MvsEnableCmd | Y0.4 | BOOL | DO | Output | Machine 1 MVS661 enable / system on
M1 | xM1SystemOnRelayCmd | Y0.5 | BOOL | DO | Output | Machine 1 system on relay output
M1 | xM1FaultRelayCmd | Y0.6 | BOOL | DO | Output | Machine 1 manual fault relay output
M1 | xM1OilInletSolValve1Cmd | Y0.7 | BOOL | DO | Output | Machine 1 compressor oil inlet solenoid 1
M1 | xM1OilInletSolValve2Cmd | Y0.8 | BOOL | DO | Output | Machine 1 compressor oil inlet solenoid 2
M1 | xM1OilInletSolValve3Cmd | Y0.9 | BOOL | DO | Output | Machine 1 compressor oil inlet solenoid 3 / aux
M1 | xM1OilInletSolValve4Cmd | Y0.10 | BOOL | DO | Output | Machine 1 compressor oil inlet solenoid 4
M1 | xM1StartLampCmd | Y0.11 | BOOL | DO | Output | Machine 1 green start lamp
M1 | xM1FaultLampCmd | Y0.12 | BOOL | DO | Output | Machine 1 red fault lamp
M1 | xM1StopLampCmd | Y0.13 | BOOL | DO | Output | Machine 1 stop lamp
M2 | xM2EvapPumpCmd | Y0.14 | BOOL | DO | Output | Machine 2 evaporator pump command
M2 | xM2CondPumpCmd | Y0.15 | BOOL | DO | Output | Machine 2 condenser pump command
M2 | xM2ExhaustFanCmd | Y0.16 | BOOL | DO | Output | Machine 2 machine room exhaust fan command
M2 | xM2CompRunCmd | Y0.17 | BOOL | DO | Output | Machine 2 compressor run output signal
M2 | xM2TwoWayValveCmd | Y0.18 | BOOL | DO | Output | Machine 2 two-way valve command
M2 | xM2MvsEnableCmd | Y0.19 | BOOL | DO | Output | Machine 2 MVS661 enable / system on
M2 | xM2SystemOnRelayCmd | Y0.20 | BOOL | DO | Output | Machine 2 system on relay output
M2 | xM2FaultRelayCmd | Y0.21 | BOOL | DO | Output | Machine 2 manual fault relay output
M2 | xM2OilInletSolValve1Cmd | Y0.22 | BOOL | DO | Output | Machine 2 compressor oil inlet solenoid 1
M2 | xM2OilInletSolValve2Cmd | Y0.23 | BOOL | DO | Output | Machine 2 compressor oil inlet solenoid 2
M2 | xM2OilInletSolValve3Cmd | Y0.24 | BOOL | DO | Output | Machine 2 compressor oil inlet solenoid 3 / aux
M2 | xM2OilInletSolValve4Cmd | Y0.25 | BOOL | DO | Output | Machine 2 compressor oil inlet solenoid 4
M2 | xM2StartLampCmd | Y0.26 | BOOL | DO | Output | Machine 2 green start lamp
M2 | xM2FaultLampCmd | Y0.27 | BOOL | DO | Output | Machine 2 red fault lamp
M2 | xM2StopLampCmd | Y0.28 | BOOL | DO | Output | Machine 2 stop lamp

## ANALOG İNPUT
AREA | Recommended_Variable | Current_IO | DataType | Signal_Class | Direction | Description_EN
M1 | rM1EvapWaterOutFlowOrTemp |  | REAL | AI | Analog Input | Machine 1 evaporator water outlet sensor 1
M1 | rM1ConWaterOutFlowOrTemp |  | REAL | AI | Analog Input | Machine 1 condenser water outlet sensor 1
M1 | rM1LiquidLevel_pct |  | REAL | AI | Analog Input | Machine 1 liquid level transmitter
M1 | rM1Pdis_bar |  | REAL | AI | Analog Input | Machine 1 compressor discharge pressure
M1 | rM1Psuc_bar |  | REAL | AI | Analog Input | Machine 1 suction pressure
M1 | rM1CompBodyTemp_C |  | REAL | AI | Analog Input | Machine 1 compressor body temperature (NTC)
M1 | rM1EvapWaterOutTemp_C |  | REAL | AI | Analog Input | Machine 1 evaporator water outlet temperature
M1 | rM1EvapWaterInTemp_C |  | REAL | AI | Analog Input | Machine 1 evaporator water inlet temperature
M1 | rM1CondWaterOutTemp_C |  | REAL | AI | Analog Input | Machine 1 condenser water outlet temperature
M1 | rM1CondWaterInTemp_C |  | REAL | AI | Analog Input | Machine 1 condenser water inlet temperature
M1 | rM1OilTemp_C |  | REAL | RTD | Analog Input | Machine 1 oil temperature PT1000
M1 | rM1SuctionTemp_C |  | REAL | RTD | Analog Input | Machine 1 suction temperature PT1000
M1 | rM1DischargeTemp_C |  | REAL | RTD | Analog Input | Machine 1 discharge temperature PT1000
M1 | rM1ViValvePos_pct |  | REAL | AI | Analog Input | Machine 1 MVS661 valve position feedback
M1 | rM1ExtSetpointInput_C |  | REAL | AI | Analog Input | Machine 1 external analog setpoint input
M2 | rM2EvapWaterOutFlowOrTemp |  | REAL | AI | Analog Input | Machine 2 evaporator water outlet sensor 1
M2 | rM2ConWaterOutFlowOrTemp |  | REAL | AI | Analog Input | Machine 2 condenser water outlet sensor 1
M2 | rM2LiquidLevel_pct |  | REAL | AI | Analog Input | Machine 2 liquid level transmitter
M2 | rM2Pdis_bar |  | REAL | AI | Analog Input | Machine 2 compressor discharge pressure
M2 | rM2Psuc_bar |  | REAL | AI | Analog Input | Machine 2 suction pressure
M2 | rM2CompBodyTemp_C |  | REAL | AI | Analog Input | Machine 2 compressor body temperature (NTC)
M2 | rM2EvapWaterOutTemp_C |  | REAL | AI | Analog Input | Machine 2 evaporator water outlet temperature
M2 | rM2EvapWaterInTemp_C |  | REAL | AI | Analog Input | Machine 2 evaporator water inlet temperature
M2 | rM2CondWaterOutTemp_C |  | REAL | AI | Analog Input | Machine 2 condenser water outlet temperature
M2 | rM2CondWaterInTemp_C |  | REAL | AI | Analog Input | Machine 2 condenser water inlet temperature
M2 | rM2OilTemp_C |  | REAL | RTD | Analog Input | Machine 2 oil temperature PT1000
M2 | rM2SuctionTemp_C |  | REAL | RTD | Analog Input | Machine 2 suction temperature PT1000
M2 | rM2DischargeTemp_C |  | REAL | RTD | Analog Input | Machine 2 discharge temperature PT1000
M2 | rM2ViValvePos_pct |  | REAL | AI | Analog Input | Machine 2 MVS661 valve position feedback
M2 | rM2ExtSetpointInput_C |  | REAL | AI | Analog Input | Machine 2 external analog setpoint input

## Analog Output
AREA | Recommended_Variable | Current_IO | DataType | Signal_Class | Direction | Description_EN
M1 | rM1CompFreqRefOut_Hz |  | REAL | AO | Analog Output | Machine 1 compressor inverter speed reference output
M1 | rM1ViValveCmd_pct |  | REAL | AO | Analog Output | Machine 1 MVS661 valve command
M2 | rM2CompFreqRefOut_Hz |  | REAL | AO | Analog Output | Machine 2 compressor inverter speed reference output
M2 | rM2ViValveCmd_pct |  | REAL | AO | Analog Output | Machine 2 MVS661 valve command