## README
Project | SBB Volta Nord – NH3 heat pump control variable master list
Purpose | Unified variable list for PLC/HMI/control programming. Can be handed to any programmer so everyone works with the same naming and structure.
Basis | Based on uploaded control wiring PDF, compressor documentation, and template screenshots.
Important | This workbook is a programming master list, not a final commissioned I/O protocol. Rows marked 'VERIFY' must be checked against final hardware and terminal list.
PLC architecture | PLC-M1 = Heat Pump 1, PLC-M2 = Heat Pump 2, PLC-SAFE = safety/gas/emergency, HMI-PLC = HMI / common interface
Naming rule | Prefix + Area + Equipment + Signal, e.g. xM1CompPermissive, rM2Psuc_bar, uiSafeAlarmId
Datatype prefixes | x=BOOL, i=INT, ui=UINT, di=DINT, r=REAL, t=TIME, e=ENUM, st=STRUCT
Signal groups | CMD = command, STS = status, AI = analog input, AO = analog output, PAR = parameter, ALM = alarm, LOG = internal logic
Recommended process | 1) Freeze names here 2) Map final hardware addresses 3) Build FBs 4) Build state machine 5) Build HMI tags from same list
Compressor note | Frascold manual states minimum ON time >5 min and maximum 8 starts/hour; oil flow must be reached in 10–20 s after start. Verify final compressor/VFD min/max Hz with manufacturer data before commissioning.

## Naming_Convention
Prefix | Meaning | Example | Color rule
x | BOOL / digital status or command | xM1CompRunFb | Black for logic / Blue for user-settable input
i | INT | iM1CompStartsHour | Black
ui | UINT | uiM1CompFreqCmd_Hz10 | Black
di | DINT | diEnergy_kWh | Black
r | REAL | rM1Psuc_bar | Black
t | TIME | tM1CompMinOn | Purple (control/logic)
e | ENUM / state | eM1UnitState | Purple
st | STRUCT | stM1Alarms | Purple
CMD | Command | xSysEnableCmd | Blue when operator writable
STS | Status | xSysReadySts | Black
PAR | Parameter | rM1Setpoint_C | Blue
ALM | Alarm | xM1HighPressureAlm | Orange/Red if trip
LOG | Internal logic | xM1CompPermissive | Purple

## PLC_Architecture
PLC | Scope | Controller | Main purpose | Networks / links
PLC-M1 | Heat Pump 1 | Schneider Modicon M172 + expansion | Compressor 1, pumps, machine 1 valves/sensors | CAN to expansion, I/O to FC1, local sensors, exchange with HMI/common
PLC-M2 | Heat Pump 2 | Schneider Modicon M172 + expansion | Compressor 2, pumps, machine 2 valves/sensors | CAN to expansion, I/O to FC2, local sensors, exchange with HMI/common
PLC-HMI | Common / HMI | Modicon M172 + 15.6" HMI | Operator interface, common signals, common logic bridge | HMI1/HMI2, machine 1 + machine 2 links, CAN to safety/common expansion
PLC-SAFE | Safety / gas / emergency | Schneider TM172E28R (per drawing) | Gas detection, room alarm devices, relay interfaces, safety-related global signals | Gas detectors, warning horns/lights, relay outputs to BMS/firefighter / manual fault signals

## Variable_Master
Area | PLC | Current_IO | Schema_Tag | Recommended_Variable | DataType | Signal_Class | Direction | Unit | Access | Description_EN | Description_DE | Criticality | HMI | Status | Source / Note
SYS | PLC-HMI |  |  | xSysEnableCmd | BOOL | CMD | Internal | - | RW | Global plant enable command | Anlagenfreigabe gesamt | HIGH | YES | PROPOSED | Core logic
SYS | PLC-HMI |  |  | xSysAutoModeCmd | BOOL | CMD | Internal | - | RW | Global auto mode command | Automatikbetrieb gesamt | MED | YES | PROPOSED | Core logic
SYS | PLC-HMI |  |  | xSysManualModeCmd | BOOL | CMD | Internal | - | RW | Global manual/service mode command | Hand-/Servicebetrieb gesamt | MED | YES | PROPOSED | Core logic
SYS | PLC-HMI |  |  | xSysAlarmResetCmd | BOOL | CMD | Internal | - | RW | Global alarm reset command | Alarm-Reset gesamt | HIGH | YES | PROPOSED | Core logic
SYS | PLC-HMI |  |  | xSysSafetyOk | BOOL | LOG | Internal | - | RO | Overall safety chain healthy | Sicherheitskette gesamt ok | HIGH | YES | PROPOSED | Derived from safety PLC
SYS | PLC-HMI |  |  | xSysBmsEnable | BOOL | CMD | Input | - | RW | BMS enable signal for overall plant | GA/BMS Freigabe Gesamtanlage | HIGH | YES | PROPOSED | External command
SYS | PLC-HMI |  |  | xSysHeatModeReq | BOOL | CMD | Input | - | RW | Heating mode request | Anforderung Heizbetrieb | MED | YES | PROPOSED | External / HMI
SYS | PLC-HMI |  |  | xSysCoolModeReq | BOOL | CMD | Input | - | RW | Cooling mode request | Anforderung Kühlbetrieb | MED | YES | PROPOSED | External / HMI
SYS | PLC-HMI |  |  | rSysLeavingWaterSetpoint_C | REAL | PAR | Input | °C | RW | Primary leaving water temperature setpoint | Hauptsollwert Austritt Wassertemperatur | HIGH | YES | PROPOSED | External / HMI
SYS | PLC-HMI |  |  | rSysLoadRequest_pct | REAL | PAR | Input | % | RW | Overall load request / capacity request | Lastanforderung / Leistungsanforderung | MED | YES | PROPOSED | Optional logic variable
SYS | PLC-HMI |  |  | xLeadIsM1 | BOOL | LOG | Internal | - | RW | Machine 1 selected as lead unit | Maschine 1 ist Führungsmaschine | MED | YES | PROPOSED | Lead/lag logic
SYS | PLC-HMI |  |  | xLeadIsM2 | BOOL | LOG | Internal | - | RW | Machine 2 selected as lead unit | Maschine 2 ist Führungsmaschine | MED | YES | PROPOSED | Lead/lag logic
SYS | PLC-HMI |  |  | xLagStartReq | BOOL | LOG | Internal | - | RO | Second unit start request due to load or failover | Anforderung Zuschaltung zweite Maschine | HIGH | YES | PROPOSED | Lead/lag logic
SYS | PLC-HMI |  |  | xFailoverReq | BOOL | LOG | Internal | - | RO | Failover request because lead unit unavailable | Failover-Anforderung bei Ausfall Führungsmaschine | HIGH | YES | PROPOSED | Lead/lag logic
SYS | PLC-HMI |  |  | eSysPlantState | ENUM | STS | Internal | - | RO | Overall plant state | Gesamtanlagenzustand | MED | YES | PROPOSED | Suggested enum
SYS | PLC-HMI |  |  | uiSysAlarmId | UINT | ALM | Internal | - | RO | Overall active alarm id | Aktive Alarm-ID Gesamtanlage | MED | YES | PROPOSED | Alarm management
SYS | PLC-HMI |  |  | xSysAnyTrip | BOOL | ALM | Internal | - | RO | Any active plant trip | Mindestens eine aktive Gesamtauslösung | HIGH | YES | PROPOSED | Alarm management
SYS | PLC-HMI |  |  | xSysReadySts | BOOL | STS | Internal | - | RO | Plant ready for operation | Anlage betriebsbereit | MED | YES | PROPOSED | Derived
SYS | PLC-HMI |  |  | xSysRunSts | BOOL | STS | Internal | - | RO | Plant in run mode | Anlage läuft | MED | YES | PROPOSED | Derived
SYS | PLC-HMI |  |  | tSysLeadRotate | TIME | PAR | Internal | h | RW | Lead/lag rotation interval | Intervall Führungsmaschinenwechsel | LOW | YES | PROPOSED | Optional
M1 | PLC-M1 |  |  | xM1EnableCmd | BOOL | CMD | Internal | - | RW | Machine 1 enable command | Freigabe Machine 1 | HIGH | YES | PROPOSED | Unit command
M1 | PLC-M1 |  |  | xM1AutoCmd | BOOL | CMD | Internal | - | RW | Machine 1 auto mode command | Automatik Machine 1 | MED | YES | PROPOSED | Unit command
M1 | PLC-M1 |  |  | xM1ManualCmd | BOOL | CMD | Internal | - | RW | Machine 1 manual mode command | Handbetrieb Machine 1 | MED | YES | PROPOSED | Unit command
M1 | PLC-M1 |  |  | xM1StartCmd | BOOL | CMD | Internal | - | RW | Machine 1 start command | Startbefehl Machine 1 | HIGH | YES | PROPOSED | From BMS / HMI
M1 | PLC-M1 |  |  | xM1StopCmd | BOOL | CMD | Internal | - | RW | Machine 1 stop command | Stopbefehl Machine 1 | HIGH | YES | PROPOSED | From BMS / HMI
M1 | PLC-M1 |  |  | xM1AlarmResetCmd | BOOL | CMD | Internal | - | RW | Machine 1 alarm reset | Alarmreset Machine 1 | HIGH | YES | PROPOSED | HMI
M1 | PLC-M1 |  |  | rM1LeavingWaterSetpoint_C | REAL | PAR | Input | °C | RW | Machine 1 leaving water setpoint | Sollwert Austritt Wasser Machine 1 | HIGH | YES | PROPOSED | External setpoint / HMI
M1 | PLC-M1 |  |  | rM1CompFreqMin_Hz | REAL | PAR | Internal | Hz | RW | Machine 1 compressor minimum frequency | Mindestfrequenz Verdichter Machine 1 | HIGH | YES | PROPOSED | Verify with compressor/VFD
M1 | PLC-M1 |  |  | rM1CompFreqMax_Hz | REAL | PAR | Internal | Hz | RW | Machine 1 compressor maximum frequency | Maximalfrequenz Verdichter Machine 1 | HIGH | YES | PROPOSED | Verify with compressor/VFD
M1 | PLC-M1 |  |  | tM1CompMinOn | TIME | PAR | Internal | s | RW | Machine 1 compressor minimum on time | Mindest-Einzeit Verdichter Machine 1 | HIGH | YES | PROPOSED | Frascold >5 min
M1 | PLC-M1 |  |  | tM1CompMinOff | TIME | PAR | Internal | s | RW | Machine 1 compressor minimum off time | Mindest-Auszeit Verdichter Machine 1 | HIGH | YES | PROPOSED | Protect motor/oil
M1 | PLC-M1 |  |  | iM1CompMaxStartsPerHour | INT | PAR | Internal | 1/h | RW | Machine 1 compressor max starts per hour | Max. Starts pro Stunde Verdichter Machine 1 | HIGH | YES | PROPOSED | Frascold max 8/h
M1 | PLC-M1 |  |  | xM1Permissive | BOOL | LOG | Internal | - | RO | Machine 1 overall permissive | Gesamtfreigabe Machine 1 | HIGH | YES | PROPOSED | AND of interlocks
M1 | PLC-M1 |  |  | xM1StartPermissive | BOOL | LOG | Internal | - | RO | Machine 1 start permissive | Startfreigabe Machine 1 | HIGH | YES | PROPOSED | Interlock result
M1 | PLC-M1 |  |  | xM1RunPermissive | BOOL | LOG | Internal | - | RO | Machine 1 run permissive | Lauffreigabe Machine 1 | HIGH | YES | PROPOSED | Interlock result
M1 | PLC-M1 |  |  | xM1Trip | BOOL | ALM | Internal | - | RO | Machine 1 trip active | Trip Machine 1 aktiv | HIGH | YES | PROPOSED | Trip result
M1 | PLC-M1 |  |  | eM1UnitState | ENUM | STS | Internal | - | RO | Machine 1 unit state | Zustand Machine 1 | MED | YES | PROPOSED | Suggested state machine
M1 | PLC-M1 |  |  | uiM1AlarmId | UINT | ALM | Internal | - | RO | Machine 1 active alarm id | Aktive Alarm-ID Machine 1 | MED | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | rM1CapacityPct | REAL | STS | Internal | % | RO | Machine 1 current capacity | Aktuelle Leistung Machine 1 | MED | YES | PROPOSED | Derived
M1 | PLC-M1 |  |  | rM1CompFreqCmd_Hz | REAL | LOG | Internal | Hz | RO | Machine 1 compressor frequency command | Frequenzsollwert Verdichter Machine 1 | HIGH | YES | PROPOSED | PID output
M1 | PLC-M1 |  |  | rM1PidOut_pct | REAL | LOG | Internal | % | RO | Machine 1 PID output | PID-Ausgang Machine 1 | MED | YES | PROPOSED | Logic
M1 | PLC-M1 |  |  | xM1PumpDownReq | BOOL | LOG | Internal | - | RO | Machine 1 pump-down request | Pump-down Anforderung Machine 1 | MED | YES | PROPOSED | Optional strategy
M1 | PLC-M1 |  |  | xM1OilHeatReady | BOOL | LOG | Internal | - | RO | Machine 1 oil heater / oil temperature ready | Ölheizung/Öltemperatur bereit Machine 1 | HIGH | YES | PROPOSED | Start interlock
M1 | PLC-M1 | A1-AO1 | FC1 | rM1CompFreqRefOut_Hz | REAL | AO | Output | Hz | RO | Machine 1 compressor inverter speed reference output | FU-Sollwert Verdichter Machine 1 | HIGH | YES | FROM SCHEMA | Compressor page
M1 | PLC-M1 | A1-DI9 | FC1 | xM1CompDriveRunFb | BOOL | DI | Input | - | RO | Machine 1 compressor drive run feedback | FU Laufmeldung Verdichter Machine 1 | HIGH | YES | FROM SCHEMA | Compressor page / verify RO mapping
M1 | PLC-M1 | A1-DI10 | FC1 | xM1CompDriveFaultFb | BOOL | DI | Input | - | RO | Machine 1 compressor drive fault feedback | FU Störmeldung Verdichter Machine 1 | HIGH | YES | FROM SCHEMA | Compressor page / verify RO mapping
M1 | PLC-M1-EXP | A4-AI8 | MT1 / HT1 | rM1CompMotorTemp_C | REAL | AI | Input | °C | RO | Machine 1 compressor motor / thermal protection analog value | Motortemperatur / Thermoschutz Verdichter Machine 1 | HIGH | YES | VERIFY | Compressor page
M1 | PLC-M1 |  | FC relay | xM1CompRunCmd | BOOL | DO | Output | - | RO | Machine 1 compressor run command to drive | Start/Freigabe Verdichter Machine 1 | HIGH | YES | PROPOSED | Usually via FB / drive comms
M1 | PLC-M1 |  | FC analogue | rM1CompActualFreq_Hz | REAL | STS | Input | Hz | RO | Machine 1 compressor actual frequency | Istfrequenz Verdichter Machine 1 | MED | YES | PROPOSED | If read via comms
M1 | PLC-M1 |  | FC analogue | rM1CompCurrent_A | REAL | STS | Input | A | RO | Machine 1 compressor current | Verdichterstrom Machine 1 | MED | YES | PROPOSED | If read via comms
M1 | PLC-M1 |  | FC analogue | rM1CompPower_kW | REAL | STS | Input | kW | RO | Machine 1 compressor electrical power | Elektrische Leistung Verdichter Machine 1 | MED | YES | PROPOSED | If read via comms
M1 | PLC-M1 |  | FC analogue | uiM1CompDriveAlarmCode | UINT | ALM | Input | - | RO | Machine 1 compressor drive alarm code | FU Alarmcode Verdichter Machine 1 | MED | YES | PROPOSED | If read via comms
M1 | PLC-M1 | A1-DI11 | M1_LLSW1 | xM1LiquidLowLevelSw | BOOL | DI | Input | - | RO | Machine 1 liquid low level switch | Flüssigkeit Unter-Niveau Machine 1 | MED | YES | FROM SCHEMA | Universal 1
M1 | PLC-M1 | A1-DI12 | M1_HLSW1 | xM1LiquidHighLevelSw | BOOL | DI | Input | - | RO | Machine 1 liquid high level switch | Flüssigkeit Ober-Niveau Machine 1 | MED | YES | FROM SCHEMA | Universal 1
M1 | PLC-M1 | A1-AI1 | M1_FT1 | rM1EvapWaterOutFlowOrTemp | REAL | AI | Input | TBD | RO | Machine 1 evaporator water outlet sensor 1 | Sensor Verdampferwasser Austritt 1 Machine 1 | MED | YES | VERIFY | Universal 1
M1 | PLC-M1 | A1-AI2 | M1_FT2 | rM1EvapWaterOutFlowOrTemp2 | REAL | AI | Input | TBD | RO | Machine 1 evaporator water outlet sensor 2 | Sensor Verdampferwasser Austritt 2 Machine 1 | MED | YES | VERIFY | Universal 1
M1 | PLC-M1 | VERIFY | M1_LT1 | rM1LiquidLevel_pct | REAL | AI | Input | % | RO | Machine 1 liquid level transmitter | Füllstandssonde Machine 1 | MED | YES | FROM SCHEMA | Universal 2; exact channel verify
M1 | PLC-M1 | VERIFY | M1_PT1 | rM1Pdis_bar | REAL | AI | Input | bar | RO | Machine 1 compressor discharge pressure | Verdichter Austrittsdruck Machine 1 | HIGH | YES | FROM SCHEMA | Universal 2; exact channel verify
M1 | PLC-M1 | VERIFY | M1_PT2 | rM1Psuc_bar | REAL | AI | Input | bar | RO | Machine 1 suction pressure | Saugdruck Machine 1 | HIGH | YES | FROM SCHEMA | Universal 2; exact channel verify
M1 | PLC-M1 | VERIFY | M1_NTC1 | rM1CompBodyTemp_C | REAL | AI | Input | °C | RO | Machine 1 compressor body temperature (NTC) | Verdichtertemperatur NTC Machine 1 | MED | YES | FROM SCHEMA | Universal 3
M1 | PLC-M1 | VERIFY | M1_NTC2 | rM1EvapWaterOutTemp_C | REAL | AI | Input | °C | RO | Machine 1 evaporator water outlet temperature | Verdampfer Wasser Austritt Temp Machine 1 | HIGH | YES | FROM SCHEMA | Universal 3
M1 | PLC-M1 | VERIFY | M1_NTC3 | rM1EvapWaterInTemp_C | REAL | AI | Input | °C | RO | Machine 1 evaporator water inlet temperature | Verdampfer Wasser Eintritt Temp Machine 1 | HIGH | YES | FROM SCHEMA | Universal 3
M1 | PLC-M1 | VERIFY | M1_NTC4 | rM1CondWaterOutTemp_C | REAL | AI | Input | °C | RO | Machine 1 condenser water outlet temperature | Verflüssiger Wasser Austritt Temp Machine 1 | HIGH | YES | FROM SCHEMA | Universal 3
M1 | PLC-M1 | VERIFY | M1_NTC5 | rM1CondWaterInTemp_C | REAL | AI | Input | °C | RO | Machine 1 condenser water inlet temperature | Verflüssiger Wasser Eintritt Temp Machine 1 | HIGH | YES | FROM SCHEMA | Universal 4
M1 | PLC-M1-EXP | VERIFY | M1_HB_TT1 | rM1OilTemp_C | REAL | AI | Input | °C | RO | Machine 1 oil temperature PT1000 | Öltemperatur PT1000 Machine 1 | HIGH | YES | FROM SCHEMA | Universal 4
M1 | PLC-M1-EXP | VERIFY | M1_HB_TT2 | rM1SuctionTemp_C | REAL | AI | Input | °C | RO | Machine 1 suction temperature PT1000 | Saugtemperatur PT1000 Machine 1 | HIGH | YES | FROM SCHEMA | Universal 4
M1 | PLC-M1-EXP | VERIFY | M1_HB_TT3 | rM1DischargeTemp_C | REAL | AI | Input | °C | RO | Machine 1 discharge temperature PT1000 | Druckgastemperatur / Austrittstemp PT1000 Machine 1 | HIGH | YES | FROM SCHEMA | Universal 4
M1 | PLC-M1-EXP | A4-DI1 | M1_FSW1 | xM1OilFlowSw | BOOL | DI | Input | - | RO | Machine 1 oil flow switch | Ölflussschalter Machine 1 | HIGH | YES | FROM SCHEMA | Universal 5
M1 | PLC-M1-EXP | A4-DI2 | M1_HPSW1 | xM1HighPressureSw | BOOL | DI | Input | - | RO | Machine 1 high pressure switch | Hochdruckschalter Machine 1 | HIGH | YES | FROM SCHEMA | Universal 5
M1 | PLC-M1-EXP | A4-DI3 | M1_LPSW1 | xM1LowPressureSw | BOOL | DI | Input | - | RO | Machine 1 low pressure switch | Niederdruckschalter Machine 1 | HIGH | YES | FROM SCHEMA | Universal 5
M1 | PLC-M1-EXP | A4-DI4 | M1_TLLSW1 | xM1OilTankLowLevelSw | BOOL | DI | Input | - | RO | Machine 1 oil tank low level switch | Öltank Niveau-Schalter Machine 1 | HIGH | YES | FROM SCHEMA | Universal 5
M1 | PLC-M1-EXP | A4-AI5 | X6 analogue | rM1ExtSetpointInput_C | REAL | AI | Input | °C | RO | Machine 1 external analog setpoint input | Externer analoger Sollwert Machine 1 | MED | YES | FROM SCHEMA | Universal 6 / customer setpoint
M1 | PLC-M1-EXP | A4-AI6 | BG01-101 | rM1FlowSwitch101Raw | REAL | AI | Input | TBD | RO | Machine 1 flow monitor raw signal 101 | Rohsignal Strömungswächter 101 Machine 1 | LOW | NO | VERIFY | Universal 6
M1 | PLC-M1-EXP | A4-AI7 | BG01-102 | rM1FlowSwitch102Raw | REAL | AI | Input | TBD | RO | Machine 1 flow monitor raw signal 102 | Rohsignal Strömungswächter 102 Machine 1 | LOW | NO | VERIFY | Universal 6
M1 | PLC-M1 | A1-DO1 | KM1 | xM1EvapPumpCmd | BOOL | DO | Output | - | RO | Machine 1 evaporator pump command | Befehl Verdampferpumpe Machine 1 | HIGH | YES | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO2 | KM2 | xM1CondPumpCmd | BOOL | DO | Output | - | RO | Machine 1 condenser pump command | Befehl Kondensatorpumpe Machine 1 | HIGH | YES | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO3 | KA1 | xM1ExhaustFanCmd | BOOL | DO | Output | - | RO | Machine 1 machine room exhaust fan command | Befehl Abluftventilator Machine 1 | HIGH | YES | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO4 | R valve | xM1TwoWayValveCmd | BOOL | DO | Output | - | RO | Machine 1 two-way valve command | Befehl 2-Wege-Ventil Machine 1 | MED | YES | FROM SCHEMA | Digital output 1 / valve page
M1 | PLC-M1 | A1-DO5 | R MVS661 | xM1MvsEnableCmd | BOOL | DO | Output | - | RO | Machine 1 MVS661 enable / system on | MVS661 Freigabe / System EIN Machine 1 | MED | YES | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO6 | R fault relay | xM1FaultRelayCmd | BOOL | DO | Output | - | RO | Machine 1 manual fault relay output | Störmelder Ausgang Machine 1 | MED | YES | FROM SCHEMA | Digital output 1 / customer page
M1 | PLC-M1 | A1-DO7 | R customer on | xM1SystemOnRelayCmd | BOOL | DO | Output | - | RO | Machine 1 system on relay output | Anlage EIN Relais Machine 1 | MED | YES | FROM SCHEMA | Digital output 1 / customer page
M1 | PLC-M1 | A1-DO8 | spare | xM1SpareOut1 | BOOL | DO | Output | - | RO | Machine 1 spare output 1 | Reserveausgang 1 Machine 1 | LOW | NO | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO9 | spare | xM1SpareOut2 | BOOL | DO | Output | - | RO | Machine 1 spare output 2 | Reserveausgang 2 Machine 1 | LOW | NO | FROM SCHEMA | Digital output 1
M1 | PLC-M1 | A1-DO10 | SV1 | xM1OilInletSolValve1Cmd | BOOL | DO | Output | - | RO | Machine 1 compressor oil inlet solenoid 1 | Öleinlass Magnetventil 1 Machine 1 | MED | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1 | A1-DO11 | SV2 | xM1OilInletSolValve2Cmd | BOOL | DO | Output | - | RO | Machine 1 compressor oil inlet solenoid 2 | Öleinlass Magnetventil 2 Machine 1 | MED | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1 | A1-DO12 | SV3 | xM1OilInletSolValve3Cmd | BOOL | DO | Output | - | RO | Machine 1 compressor oil inlet solenoid 3 / aux | Öleinlass Magnetventil 3 / Zusatz Machine 1 | MED | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1-EXP | A4-DO1 | P1 | xM1StartLampCmd | BOOL | DO | Output | - | RO | Machine 1 green start lamp | Startlampe grün Machine 1 | LOW | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1-EXP | A4-DO2 | P2 | xM1FaultLampCmd | BOOL | DO | Output | - | RO | Machine 1 red fault lamp | Störlampe rot Machine 1 | LOW | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1-EXP | A4-DO3 | P3 | xM1StopLampCmd | BOOL | DO | Output | - | RO | Machine 1 stop lamp | Stopplampe Machine 1 | LOW | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1-EXP | A4-DO4 | SV4 | xM1OilInletSolValve4Cmd | BOOL | DO | Output | - | RO | Machine 1 compressor oil inlet solenoid 4 | Öleinlass Magnetventil 4 Machine 1 | MED | YES | FROM SCHEMA | Digital output 2
M1 | PLC-M1 | A1-AO2 | MVS661 | rM1ViValveCmd_pct | REAL | AO | Output | % | RO | Machine 1 MVS661 valve command | Stellsignal MVS661 Machine 1 | MED | YES | FROM SCHEMA | MVS661 page
M1 | PLC-M1-EXP | A4-AI8 | MVS661 | rM1ViValvePos_pct | REAL | AI | Input | % | RO | Machine 1 MVS661 valve position feedback | Rückmeldung MVS661 Machine 1 | MED | YES | FROM SCHEMA | MVS661 page
M1 | PLC-M1-EXP | A4-DI5 | Customer CR1/CR3 | xM1BmsStartEnableIn | BOOL | DI | Input | - | RO | Machine 1 external BMS start enable input | Externe Startfreigabe BMS Machine 1 | HIGH | YES | FROM SCHEMA | Customer page
M1 | PLC-M1-EXP | A4-DI6 | Customer CR2/CR4 | xM1BmsHeatCoolSelectIn | BOOL | DI | Input | - | RO | Machine 1 external heating/cooling select input | Externe Heiz/Kühl-Umschaltung Machine 1 | MED | YES | FROM SCHEMA | Customer page
M1 | PLC-M1 |  |  | rM1CompHours_h | REAL | STS | Internal | h | RO | Machine 1 compressor operating hours | Betriebsstunden Verdichter Machine 1 | LOW | YES | PROPOSED | Runtime counter
M1 | PLC-M1 |  |  | iM1CompStartsCounter | INT | STS | Internal | count | RO | Machine 1 compressor starts counter | Startzähler Verdichter Machine 1 | LOW | YES | PROPOSED | Counter
M1 | PLC-M1 |  |  | xM1CompStartReq | BOOL | LOG | Internal | - | RO | Machine 1 compressor start request | Startanforderung Verdichter Machine 1 | HIGH | YES | PROPOSED | Core logic
M1 | PLC-M1 |  |  | xM1CompRunFb | BOOL | LOG | Internal | - | RO | Machine 1 compressor run feedback (unified) | Laufmeldung Verdichter vereinheitlicht Machine 1 | HIGH | YES | PROPOSED | Unified status
M1 | PLC-M1 |  |  | xM1CompTripHp | BOOL | ALM | Internal | - | RO | Machine 1 high pressure trip | Hochdruck-Trip Machine 1 | HIGH | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | xM1CompTripLp | BOOL | ALM | Internal | - | RO | Machine 1 low pressure trip | Niederdruck-Trip Machine 1 | HIGH | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | xM1CompTripOilFlow | BOOL | ALM | Internal | - | RO | Machine 1 oil flow trip | Ölfluss-Trip Machine 1 | HIGH | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | xM1CompTripMotor | BOOL | ALM | Internal | - | RO | Machine 1 motor / thermal trip | Motor-/Thermoschutz-Trip Machine 1 | HIGH | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | xM1CompTripSafety | BOOL | ALM | Internal | - | RO | Machine 1 safety PLC trip | Sicherheits-Trip Machine 1 | HIGH | YES | PROPOSED | Alarm logic
M1 | PLC-M1 |  |  | xM1EvapPumpRunReq | BOOL | LOG | Internal | - | RO | Machine 1 evaporator pump run request | Laufanforderung Verdampferpumpe Machine 1 | HIGH | YES | PROPOSED | Sequence logic
M1 | PLC-M1 |  |  | xM1CondPumpRunReq | BOOL | LOG | Internal | - | RO | Machine 1 condenser pump run request | Laufanforderung Kondensatorpumpe Machine 1 | HIGH | YES | PROPOSED | Sequence logic
M1 | PLC-M1 |  |  | xM1FlowProven | BOOL | LOG | Internal | - | RO | Machine 1 flow proven before compressor start | Durchfluss bestätigt vor Verdichterstart Machine 1 | HIGH | YES | PROPOSED | Sequence logic
M1 | PLC-M1 |  |  | tM1PumpPreRun_s | TIME | PAR | Internal | s | RW | Machine 1 pump pre-run time | Vorlaufzeit Pumpen Machine 1 | MED | YES | PROPOSED | Sequence logic
M1 | PLC-M1 |  |  | tM1PumpPostRun_s | TIME | PAR | Internal | s | RW | Machine 1 pump post-run time | Nachlaufzeit Pumpen Machine 1 | MED | YES | PROPOSED | Sequence logic
M1 | PLC-M1 |  |  | tM1OilFlowProof_s | TIME | PAR | Internal | s | RW | Machine 1 allowed time to prove oil flow | Zeitfenster Ölflussnachweis Machine 1 | HIGH | YES | PROPOSED | Frascold 10–20 s
M1 | PLC-M1 |  |  | tM1AntiShortCycle_s | TIME | PAR | Internal | s | RW | Machine 1 anti short cycle timer | Anti-Kurzzyklus Zeit Machine 1 | HIGH | YES | PROPOSED | Protection
M1 | PLC-M1 |  |  | rM1CompressionRatio | REAL | LOG | Internal | ratio | RO | Machine 1 compression ratio Pdis/Psuc | Verdichtungsverhältnis Machine 1 | MED | YES | PROPOSED | For Vi logic
M1 | PLC-M1 |  |  | xM1ViHighRatioMode | BOOL | LOG | Internal | - | RO | Machine 1 high ratio mode for Vi solenoid strategy | High-Ratio Modus für Vi-Logik Machine 1 | MED | YES | PROPOSED | Frascold table threshold 2.7 ± deadband
M1 | PLC-M1 |  |  | xM1HeatingSeason | BOOL | LOG | Internal | - | RO | Machine 1 heating season / mode active | Heizbetrieb aktiv Machine 1 | MED | YES | PROPOSED | Mode logic
M1 | PLC-M1 |  |  | xM1CoolingSeason | BOOL | LOG | Internal | - | RO | Machine 1 cooling season / mode active | Kühlbetrieb aktiv Machine 1 | MED | YES | PROPOSED | Mode logic
M1 | PLC-M1 |  |  | xM1HealthyForLead | BOOL | LOG | Internal | - | RO | Machine 1 unit healthy and available for lead role | Maschine gesund und für Führung verfügbar Machine 1 | MED | YES | PROPOSED | Lead/lag
M1 | PLC-M1 |  |  | xM1HealthyForLag | BOOL | LOG | Internal | - | RO | Machine 1 unit healthy and available for lag role | Maschine gesund und für Zuschaltung verfügbar Machine 1 | MED | YES | PROPOSED | Lead/lag
M2 | PLC-M2 |  |  | xM2EnableCmd | BOOL | CMD | Internal | - | RW | Machine 2 enable command | Freigabe Machine 2 | HIGH | YES | PROPOSED | Unit command
M2 | PLC-M2 |  |  | xM2AutoCmd | BOOL | CMD | Internal | - | RW | Machine 2 auto mode command | Automatik Machine 2 | MED | YES | PROPOSED | Unit command
M2 | PLC-M2 |  |  | xM2ManualCmd | BOOL | CMD | Internal | - | RW | Machine 2 manual mode command | Handbetrieb Machine 2 | MED | YES | PROPOSED | Unit command
M2 | PLC-M2 |  |  | xM2StartCmd | BOOL | CMD | Internal | - | RW | Machine 2 start command | Startbefehl Machine 2 | HIGH | YES | PROPOSED | From BMS / HMI
M2 | PLC-M2 |  |  | xM2StopCmd | BOOL | CMD | Internal | - | RW | Machine 2 stop command | Stopbefehl Machine 2 | HIGH | YES | PROPOSED | From BMS / HMI
M2 | PLC-M2 |  |  | xM2AlarmResetCmd | BOOL | CMD | Internal | - | RW | Machine 2 alarm reset | Alarmreset Machine 2 | HIGH | YES | PROPOSED | HMI
M2 | PLC-M2 |  |  | rM2LeavingWaterSetpoint_C | REAL | PAR | Input | °C | RW | Machine 2 leaving water setpoint | Sollwert Austritt Wasser Machine 2 | HIGH | YES | PROPOSED | External setpoint / HMI
M2 | PLC-M2 |  |  | rM2CompFreqMin_Hz | REAL | PAR | Internal | Hz | RW | Machine 2 compressor minimum frequency | Mindestfrequenz Verdichter Machine 2 | HIGH | YES | PROPOSED | Verify with compressor/VFD
M2 | PLC-M2 |  |  | rM2CompFreqMax_Hz | REAL | PAR | Internal | Hz | RW | Machine 2 compressor maximum frequency | Maximalfrequenz Verdichter Machine 2 | HIGH | YES | PROPOSED | Verify with compressor/VFD
M2 | PLC-M2 |  |  | tM2CompMinOn | TIME | PAR | Internal | s | RW | Machine 2 compressor minimum on time | Mindest-Einzeit Verdichter Machine 2 | HIGH | YES | PROPOSED | Frascold >5 min
M2 | PLC-M2 |  |  | tM2CompMinOff | TIME | PAR | Internal | s | RW | Machine 2 compressor minimum off time | Mindest-Auszeit Verdichter Machine 2 | HIGH | YES | PROPOSED | Protect motor/oil
M2 | PLC-M2 |  |  | iM2CompMaxStartsPerHour | INT | PAR | Internal | 1/h | RW | Machine 2 compressor max starts per hour | Max. Starts pro Stunde Verdichter Machine 2 | HIGH | YES | PROPOSED | Frascold max 8/h
M2 | PLC-M2 |  |  | xM2Permissive | BOOL | LOG | Internal | - | RO | Machine 2 overall permissive | Gesamtfreigabe Machine 2 | HIGH | YES | PROPOSED | AND of interlocks
M2 | PLC-M2 |  |  | xM2StartPermissive | BOOL | LOG | Internal | - | RO | Machine 2 start permissive | Startfreigabe Machine 2 | HIGH | YES | PROPOSED | Interlock result
M2 | PLC-M2 |  |  | xM2RunPermissive | BOOL | LOG | Internal | - | RO | Machine 2 run permissive | Lauffreigabe Machine 2 | HIGH | YES | PROPOSED | Interlock result
M2 | PLC-M2 |  |  | xM2Trip | BOOL | ALM | Internal | - | RO | Machine 2 trip active | Trip Machine 2 aktiv | HIGH | YES | PROPOSED | Trip result
M2 | PLC-M2 |  |  | eM2UnitState | ENUM | STS | Internal | - | RO | Machine 2 unit state | Zustand Machine 2 | MED | YES | PROPOSED | Suggested state machine
M2 | PLC-M2 |  |  | uiM2AlarmId | UINT | ALM | Internal | - | RO | Machine 2 active alarm id | Aktive Alarm-ID Machine 2 | MED | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | rM2CapacityPct | REAL | STS | Internal | % | RO | Machine 2 current capacity | Aktuelle Leistung Machine 2 | MED | YES | PROPOSED | Derived
M2 | PLC-M2 |  |  | rM2CompFreqCmd_Hz | REAL | LOG | Internal | Hz | RO | Machine 2 compressor frequency command | Frequenzsollwert Verdichter Machine 2 | HIGH | YES | PROPOSED | PID output
M2 | PLC-M2 |  |  | rM2PidOut_pct | REAL | LOG | Internal | % | RO | Machine 2 PID output | PID-Ausgang Machine 2 | MED | YES | PROPOSED | Logic
M2 | PLC-M2 |  |  | xM2PumpDownReq | BOOL | LOG | Internal | - | RO | Machine 2 pump-down request | Pump-down Anforderung Machine 2 | MED | YES | PROPOSED | Optional strategy
M2 | PLC-M2 |  |  | xM2OilHeatReady | BOOL | LOG | Internal | - | RO | Machine 2 oil heater / oil temperature ready | Ölheizung/Öltemperatur bereit Machine 2 | HIGH | YES | PROPOSED | Start interlock
M2 | PLC-M2 | A2-AO1 | FC2 | rM2CompFreqRefOut_Hz | REAL | AO | Output | Hz | RO | Machine 2 compressor inverter speed reference output | FU-Sollwert Verdichter Machine 2 | HIGH | YES | FROM SCHEMA | Compressor page
M2 | PLC-M2 | A2-DI9 | FC2 | xM2CompDriveRunFb | BOOL | DI | Input | - | RO | Machine 2 compressor drive run feedback | FU Laufmeldung Verdichter Machine 2 | HIGH | YES | FROM SCHEMA | Compressor page / verify RO mapping
M2 | PLC-M2 | A2-DI10 | FC2 | xM2CompDriveFaultFb | BOOL | DI | Input | - | RO | Machine 2 compressor drive fault feedback | FU Störmeldung Verdichter Machine 2 | HIGH | YES | FROM SCHEMA | Compressor page / verify RO mapping
M2 | PLC-M2-EXP | A5-AI8 | MT1 / HT1 | rM2CompMotorTemp_C | REAL | AI | Input | °C | RO | Machine 2 compressor motor / thermal protection analog value | Motortemperatur / Thermoschutz Verdichter Machine 2 | HIGH | YES | VERIFY | Compressor page
M2 | PLC-M2 |  | FC relay | xM2CompRunCmd | BOOL | DO | Output | - | RO | Machine 2 compressor run command to drive | Start/Freigabe Verdichter Machine 2 | HIGH | YES | PROPOSED | Usually via FB / drive comms
M2 | PLC-M2 |  | FC analogue | rM2CompActualFreq_Hz | REAL | STS | Input | Hz | RO | Machine 2 compressor actual frequency | Istfrequenz Verdichter Machine 2 | MED | YES | PROPOSED | If read via comms
M2 | PLC-M2 |  | FC analogue | rM2CompCurrent_A | REAL | STS | Input | A | RO | Machine 2 compressor current | Verdichterstrom Machine 2 | MED | YES | PROPOSED | If read via comms
M2 | PLC-M2 |  | FC analogue | rM2CompPower_kW | REAL | STS | Input | kW | RO | Machine 2 compressor electrical power | Elektrische Leistung Verdichter Machine 2 | MED | YES | PROPOSED | If read via comms
M2 | PLC-M2 |  | FC analogue | uiM2CompDriveAlarmCode | UINT | ALM | Input | - | RO | Machine 2 compressor drive alarm code | FU Alarmcode Verdichter Machine 2 | MED | YES | PROPOSED | If read via comms
M2 | PLC-M2 | A2-DI11 | M2_LLSW1 | xM2LiquidLowLevelSw | BOOL | DI | Input | - | RO | Machine 2 liquid low level switch | Flüssigkeit Unter-Niveau Machine 2 | MED | YES | FROM SCHEMA | Universal 1
M2 | PLC-M2 | A2-DI12 | M2_HLSW1 | xM2LiquidHighLevelSw | BOOL | DI | Input | - | RO | Machine 2 liquid high level switch | Flüssigkeit Ober-Niveau Machine 2 | MED | YES | FROM SCHEMA | Universal 1
M2 | PLC-M2 | A2-AI1 | M2_FT1 | rM2EvapWaterOutFlowOrTemp | REAL | AI | Input | TBD | RO | Machine 2 evaporator water outlet sensor 1 | Sensor Verdampferwasser Austritt 1 Machine 2 | MED | YES | VERIFY | Universal 1
M2 | PLC-M2 | A2-AI2 | M2_FT2 | rM2EvapWaterOutFlowOrTemp2 | REAL | AI | Input | TBD | RO | Machine 2 evaporator water outlet sensor 2 | Sensor Verdampferwasser Austritt 2 Machine 2 | MED | YES | VERIFY | Universal 1
M2 | PLC-M2 | VERIFY | M2_LT1 | rM2LiquidLevel_pct | REAL | AI | Input | % | RO | Machine 2 liquid level transmitter | Füllstandssonde Machine 2 | MED | YES | FROM SCHEMA | Universal 2; exact channel verify
M2 | PLC-M2 | VERIFY | M2_PT1 | rM2Pdis_bar | REAL | AI | Input | bar | RO | Machine 2 compressor discharge pressure | Verdichter Austrittsdruck Machine 2 | HIGH | YES | FROM SCHEMA | Universal 2; exact channel verify
M2 | PLC-M2 | VERIFY | M2_PT2 | rM2Psuc_bar | REAL | AI | Input | bar | RO | Machine 2 suction pressure | Saugdruck Machine 2 | HIGH | YES | FROM SCHEMA | Universal 2; exact channel verify
M2 | PLC-M2 | VERIFY | M2_NTC1 | rM2CompBodyTemp_C | REAL | AI | Input | °C | RO | Machine 2 compressor body temperature (NTC) | Verdichtertemperatur NTC Machine 2 | MED | YES | FROM SCHEMA | Universal 3
M2 | PLC-M2 | VERIFY | M2_NTC2 | rM2EvapWaterOutTemp_C | REAL | AI | Input | °C | RO | Machine 2 evaporator water outlet temperature | Verdampfer Wasser Austritt Temp Machine 2 | HIGH | YES | FROM SCHEMA | Universal 3
M2 | PLC-M2 | VERIFY | M2_NTC3 | rM2EvapWaterInTemp_C | REAL | AI | Input | °C | RO | Machine 2 evaporator water inlet temperature | Verdampfer Wasser Eintritt Temp Machine 2 | HIGH | YES | FROM SCHEMA | Universal 3
M2 | PLC-M2 | VERIFY | M2_NTC4 | rM2CondWaterOutTemp_C | REAL | AI | Input | °C | RO | Machine 2 condenser water outlet temperature | Verflüssiger Wasser Austritt Temp Machine 2 | HIGH | YES | FROM SCHEMA | Universal 3
M2 | PLC-M2 | VERIFY | M2_NTC5 | rM2CondWaterInTemp_C | REAL | AI | Input | °C | RO | Machine 2 condenser water inlet temperature | Verflüssiger Wasser Eintritt Temp Machine 2 | HIGH | YES | FROM SCHEMA | Universal 4
M2 | PLC-M2-EXP | VERIFY | M2_HB_TT1 | rM2OilTemp_C | REAL | AI | Input | °C | RO | Machine 2 oil temperature PT1000 | Öltemperatur PT1000 Machine 2 | HIGH | YES | FROM SCHEMA | Universal 4
M2 | PLC-M2-EXP | VERIFY | M2_HB_TT2 | rM2SuctionTemp_C | REAL | AI | Input | °C | RO | Machine 2 suction temperature PT1000 | Saugtemperatur PT1000 Machine 2 | HIGH | YES | FROM SCHEMA | Universal 4
M2 | PLC-M2-EXP | VERIFY | M2_HB_TT3 | rM2DischargeTemp_C | REAL | AI | Input | °C | RO | Machine 2 discharge temperature PT1000 | Druckgastemperatur / Austrittstemp PT1000 Machine 2 | HIGH | YES | FROM SCHEMA | Universal 4
M2 | PLC-M2-EXP | A5-DI1 | M2_FSW1 | xM2OilFlowSw | BOOL | DI | Input | - | RO | Machine 2 oil flow switch | Ölflussschalter Machine 2 | HIGH | YES | FROM SCHEMA | Universal 5
M2 | PLC-M2-EXP | A5-DI2 | M2_HPSW1 | xM2HighPressureSw | BOOL | DI | Input | - | RO | Machine 2 high pressure switch | Hochdruckschalter Machine 2 | HIGH | YES | FROM SCHEMA | Universal 5
M2 | PLC-M2-EXP | A5-DI3 | M2_LPSW1 | xM2LowPressureSw | BOOL | DI | Input | - | RO | Machine 2 low pressure switch | Niederdruckschalter Machine 2 | HIGH | YES | FROM SCHEMA | Universal 5
M2 | PLC-M2-EXP | A5-DI4 | M2_TLLSW1 | xM2OilTankLowLevelSw | BOOL | DI | Input | - | RO | Machine 2 oil tank low level switch | Öltank Niveau-Schalter Machine 2 | HIGH | YES | FROM SCHEMA | Universal 5
M2 | PLC-M2-EXP | A5-AI5 | X6 analogue | rM2ExtSetpointInput_C | REAL | AI | Input | °C | RO | Machine 2 external analog setpoint input | Externer analoger Sollwert Machine 2 | MED | YES | FROM SCHEMA | Universal 6 / customer setpoint
M2 | PLC-M2-EXP | A5-AI6 | BG01-101 | rM2FlowSwitch101Raw | REAL | AI | Input | TBD | RO | Machine 2 flow monitor raw signal 101 | Rohsignal Strömungswächter 101 Machine 2 | LOW | NO | VERIFY | Universal 6
M2 | PLC-M2-EXP | A5-AI7 | BG01-102 | rM2FlowSwitch102Raw | REAL | AI | Input | TBD | RO | Machine 2 flow monitor raw signal 102 | Rohsignal Strömungswächter 102 Machine 2 | LOW | NO | VERIFY | Universal 6
M2 | PLC-M2 | A2-DO1 | KM3 | xM2EvapPumpCmd | BOOL | DO | Output | - | RO | Machine 2 evaporator pump command | Befehl Verdampferpumpe Machine 2 | HIGH | YES | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO2 | KM4 | xM2CondPumpCmd | BOOL | DO | Output | - | RO | Machine 2 condenser pump command | Befehl Kondensatorpumpe Machine 2 | HIGH | YES | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO3 | KA2 | xM2ExhaustFanCmd | BOOL | DO | Output | - | RO | Machine 2 machine room exhaust fan command | Befehl Abluftventilator Machine 2 | HIGH | YES | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO4 | R valve | xM2TwoWayValveCmd | BOOL | DO | Output | - | RO | Machine 2 two-way valve command | Befehl 2-Wege-Ventil Machine 2 | MED | YES | FROM SCHEMA | Digital output 1 / valve page
M2 | PLC-M2 | A2-DO5 | R MVS661 | xM2MvsEnableCmd | BOOL | DO | Output | - | RO | Machine 2 MVS661 enable / system on | MVS661 Freigabe / System EIN Machine 2 | MED | YES | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO6 | R fault relay | xM2FaultRelayCmd | BOOL | DO | Output | - | RO | Machine 2 manual fault relay output | Störmelder Ausgang Machine 2 | MED | YES | FROM SCHEMA | Digital output 1 / customer page
M2 | PLC-M2 | A2-DO7 | R customer on | xM2SystemOnRelayCmd | BOOL | DO | Output | - | RO | Machine 2 system on relay output | Anlage EIN Relais Machine 2 | MED | YES | FROM SCHEMA | Digital output 1 / customer page
M2 | PLC-M2 | A2-DO8 | spare | xM2SpareOut1 | BOOL | DO | Output | - | RO | Machine 2 spare output 1 | Reserveausgang 1 Machine 2 | LOW | NO | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO9 | spare | xM2SpareOut2 | BOOL | DO | Output | - | RO | Machine 2 spare output 2 | Reserveausgang 2 Machine 2 | LOW | NO | FROM SCHEMA | Digital output 1
M2 | PLC-M2 | A2-DO10 | SV1 | xM2OilInletSolValve1Cmd | BOOL | DO | Output | - | RO | Machine 2 compressor oil inlet solenoid 1 | Öleinlass Magnetventil 1 Machine 2 | MED | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2 | A2-DO11 | SV2 | xM2OilInletSolValve2Cmd | BOOL | DO | Output | - | RO | Machine 2 compressor oil inlet solenoid 2 | Öleinlass Magnetventil 2 Machine 2 | MED | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2 | A2-DO12 | SV3 | xM2OilInletSolValve3Cmd | BOOL | DO | Output | - | RO | Machine 2 compressor oil inlet solenoid 3 / aux | Öleinlass Magnetventil 3 / Zusatz Machine 2 | MED | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2-EXP | A5-DO1 | P4 | xM2StartLampCmd | BOOL | DO | Output | - | RO | Machine 2 green start lamp | Startlampe grün Machine 2 | LOW | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2-EXP | A5-DO2 | P5 | xM2FaultLampCmd | BOOL | DO | Output | - | RO | Machine 2 red fault lamp | Störlampe rot Machine 2 | LOW | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2-EXP | A5-DO3 | P6 | xM2StopLampCmd | BOOL | DO | Output | - | RO | Machine 2 stop lamp | Stopplampe Machine 2 | LOW | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2-EXP | A5-DO4 | SV4 | xM2OilInletSolValve4Cmd | BOOL | DO | Output | - | RO | Machine 2 compressor oil inlet solenoid 4 | Öleinlass Magnetventil 4 Machine 2 | MED | YES | FROM SCHEMA | Digital output 2
M2 | PLC-M2 | A2-AO2 | MVS661 | rM2ViValveCmd_pct | REAL | AO | Output | % | RO | Machine 2 MVS661 valve command | Stellsignal MVS661 Machine 2 | MED | YES | FROM SCHEMA | MVS661 page
M2 | PLC-M2-EXP | A5-AI8 | MVS661 | rM2ViValvePos_pct | REAL | AI | Input | % | RO | Machine 2 MVS661 valve position feedback | Rückmeldung MVS661 Machine 2 | MED | YES | FROM SCHEMA | MVS661 page
M2 | PLC-M2-EXP | A5-DI5 | Customer CR1/CR3 | xM2BmsStartEnableIn | BOOL | DI | Input | - | RO | Machine 2 external BMS start enable input | Externe Startfreigabe BMS Machine 2 | HIGH | YES | FROM SCHEMA | Customer page
M2 | PLC-M2-EXP | A5-DI6 | Customer CR2/CR4 | xM2BmsHeatCoolSelectIn | BOOL | DI | Input | - | RO | Machine 2 external heating/cooling select input | Externe Heiz/Kühl-Umschaltung Machine 2 | MED | YES | FROM SCHEMA | Customer page
M2 | PLC-M2 |  |  | rM2CompHours_h | REAL | STS | Internal | h | RO | Machine 2 compressor operating hours | Betriebsstunden Verdichter Machine 2 | LOW | YES | PROPOSED | Runtime counter
M2 | PLC-M2 |  |  | iM2CompStartsCounter | INT | STS | Internal | count | RO | Machine 2 compressor starts counter | Startzähler Verdichter Machine 2 | LOW | YES | PROPOSED | Counter
M2 | PLC-M2 |  |  | xM2CompStartReq | BOOL | LOG | Internal | - | RO | Machine 2 compressor start request | Startanforderung Verdichter Machine 2 | HIGH | YES | PROPOSED | Core logic
M2 | PLC-M2 |  |  | xM2CompRunFb | BOOL | LOG | Internal | - | RO | Machine 2 compressor run feedback (unified) | Laufmeldung Verdichter vereinheitlicht Machine 2 | HIGH | YES | PROPOSED | Unified status
M2 | PLC-M2 |  |  | xM2CompTripHp | BOOL | ALM | Internal | - | RO | Machine 2 high pressure trip | Hochdruck-Trip Machine 2 | HIGH | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | xM2CompTripLp | BOOL | ALM | Internal | - | RO | Machine 2 low pressure trip | Niederdruck-Trip Machine 2 | HIGH | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | xM2CompTripOilFlow | BOOL | ALM | Internal | - | RO | Machine 2 oil flow trip | Ölfluss-Trip Machine 2 | HIGH | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | xM2CompTripMotor | BOOL | ALM | Internal | - | RO | Machine 2 motor / thermal trip | Motor-/Thermoschutz-Trip Machine 2 | HIGH | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | xM2CompTripSafety | BOOL | ALM | Internal | - | RO | Machine 2 safety PLC trip | Sicherheits-Trip Machine 2 | HIGH | YES | PROPOSED | Alarm logic
M2 | PLC-M2 |  |  | xM2EvapPumpRunReq | BOOL | LOG | Internal | - | RO | Machine 2 evaporator pump run request | Laufanforderung Verdampferpumpe Machine 2 | HIGH | YES | PROPOSED | Sequence logic
M2 | PLC-M2 |  |  | xM2CondPumpRunReq | BOOL | LOG | Internal | - | RO | Machine 2 condenser pump run request | Laufanforderung Kondensatorpumpe Machine 2 | HIGH | YES | PROPOSED | Sequence logic
M2 | PLC-M2 |  |  | xM2FlowProven | BOOL | LOG | Internal | - | RO | Machine 2 flow proven before compressor start | Durchfluss bestätigt vor Verdichterstart Machine 2 | HIGH | YES | PROPOSED | Sequence logic
M2 | PLC-M2 |  |  | tM2PumpPreRun_s | TIME | PAR | Internal | s | RW | Machine 2 pump pre-run time | Vorlaufzeit Pumpen Machine 2 | MED | YES | PROPOSED | Sequence logic
M2 | PLC-M2 |  |  | tM2PumpPostRun_s | TIME | PAR | Internal | s | RW | Machine 2 pump post-run time | Nachlaufzeit Pumpen Machine 2 | MED | YES | PROPOSED | Sequence logic
M2 | PLC-M2 |  |  | tM2OilFlowProof_s | TIME | PAR | Internal | s | RW | Machine 2 allowed time to prove oil flow | Zeitfenster Ölflussnachweis Machine 2 | HIGH | YES | PROPOSED | Frascold 10–20 s
M2 | PLC-M2 |  |  | tM2AntiShortCycle_s | TIME | PAR | Internal | s | RW | Machine 2 anti short cycle timer | Anti-Kurzzyklus Zeit Machine 2 | HIGH | YES | PROPOSED | Protection
M2 | PLC-M2 |  |  | rM2CompressionRatio | REAL | LOG | Internal | ratio | RO | Machine 2 compression ratio Pdis/Psuc | Verdichtungsverhältnis Machine 2 | MED | YES | PROPOSED | For Vi logic
M2 | PLC-M2 |  |  | xM2ViHighRatioMode | BOOL | LOG | Internal | - | RO | Machine 2 high ratio mode for Vi solenoid strategy | High-Ratio Modus für Vi-Logik Machine 2 | MED | YES | PROPOSED | Frascold table threshold 2.7 ± deadband
M2 | PLC-M2 |  |  | xM2HeatingSeason | BOOL | LOG | Internal | - | RO | Machine 2 heating season / mode active | Heizbetrieb aktiv Machine 2 | MED | YES | PROPOSED | Mode logic
M2 | PLC-M2 |  |  | xM2CoolingSeason | BOOL | LOG | Internal | - | RO | Machine 2 cooling season / mode active | Kühlbetrieb aktiv Machine 2 | MED | YES | PROPOSED | Mode logic
M2 | PLC-M2 |  |  | xM2HealthyForLead | BOOL | LOG | Internal | - | RO | Machine 2 unit healthy and available for lead role | Maschine gesund und für Führung verfügbar Machine 2 | MED | YES | PROPOSED | Lead/lag
M2 | PLC-M2 |  |  | xM2HealthyForLag | BOOL | LOG | Internal | - | RO | Machine 2 unit healthy and available for lag role | Maschine gesund und für Zuschaltung verfügbar Machine 2 | MED | YES | PROPOSED | Lead/lag
HMI | PLC-HMI |  | HMI1/HMI2 | xHmiLoginLevelService | BOOL | STS | Internal | - | RO | Service login level active | Service-Login aktiv | LOW | YES | PROPOSED | HMI
HMI | PLC-HMI |  | HMI1/HMI2 | xHmiLoginLevelAdmin | BOOL | STS | Internal | - | RO | Admin login level active | Admin-Login aktiv | LOW | YES | PROPOSED | HMI
HMI | PLC-HMI |  | HMI1/HMI2 | xHmiWriteEnableParams | BOOL | LOG | Internal | - | RO | HMI parameter write enabled | HMI Parameterschreiben freigegeben | MED | YES | PROPOSED | HMI security
HMI | PLC-HMI |  | HMI1/HMI2 | xHmiAckAllAlarmsCmd | BOOL | CMD | Internal | - | RW | Acknowledge all alarms command | Befehl alle Alarme quittieren | MED | YES | PROPOSED | HMI
HMI | PLC-HMI |  | HMI1/HMI2 | xHmiTrendEnable | BOOL | STS | Internal | - | RO | Trend logging enabled | Trendaufzeichnung aktiv | LOW | YES | PROPOSED | HMI
HMI | PLC-HMI |  | HMI1/HMI2 | rHmiSelectedSetpoint_C | REAL | PAR | Internal | °C | RW | Setpoint selected on HMI | Am HMI gewählter Sollwert | MED | YES | PROPOSED | HMI

## State_Machine
State | Purpose | Entry conditions | Main actions | Exit conditions | Key variables
0_OFF | Unit disabled / stopped | No enable, stop cmd, or global trip | Outputs off except required heaters | Enable + safety ok + auto/manual valid | xM#EnableCmd, xSysSafetyOk
10_READY | Healthy and waiting | Safety ok, no trip, interlocks healthy | Unit ready, pumps off/on per logic | Start request | xM#Permissive
20_PRELUBE_PRECHECK | Before compressor start | Start request + permissive | Check oil heater ready, anti-short-cycle done, reset runtime flags | Preconditions ok | xM#OilHeatReady, tM#AntiShortCycle_s
30_PUMPS_START | Start pumps before compressor | Precheck ok | Start evaporator + condenser pumps | Pump run proof + flow proven | xM#EvapPumpRunReq, xM#CondPumpRunReq, xM#FlowProven
40_COMP_START | Start compressor | Pumps proven and flow proven | Send drive run command, apply initial frequency, start timers | Run feedback true and oil flow proved | xM#CompStartReq, xM#CompDriveRunFb, xM#OilFlowSw
50_RUN | Normal operation | Compressor running | PID set frequency, monitor alarms, manage Vi logic, runtime and starts | Stop request / lag logic / trip | rM#CompFreqCmd_Hz, rM#CompressionRatio
60_PUMPDOWN_STOP | Controlled stop | Stop request or demand removed | Reduce frequency / execute pump-down if used, stop compressor | Compressor stopped | xM#PumpDownReq
70_PUMPS_POSTRUN | Pump afterrun | Compressor stopped | Keep pumps running for defined time | Postrun elapsed | tM#PumpPostRun_s
80_TRIP_LOCKOUT | Fault lockout | Any trip true | Immediate safe stop, keep alarms latched | Alarm reset + all fault causes clear | xM#Trip, uiM#AlarmId

## Alarm_Classes
Class | Meaning | Typical reaction | Examples
TRIP | Immediate stop / lockout | Stop compressor immediately, latch alarm, operator reset required | High pressure, safety PLC trip, oil flow fail, motor thermal
FAULT | Unit unavailable until cause clears | Stop affected function, alarm visible, may require reset | Drive fault, sensor fail critical, communication fail
WARNING | No immediate stop | Keep running if safe, alarm visible | Deviation, high discharge temp warning
INFO | Operator information | No stop, log only | Lead-lag change, manual mode active